Text for specification

Descripción
QUADRON^®Panel
parte inferior de base NH de 160 A
tornillo M8 en ambos lados
talla 00/1P, con protección contra contacto

Normas
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

datos eléctricos
intensidad de corriente nominal (IEC):	160 A
tensión nominal (IEC) AC:	690 V
tensión nominal (IEC) DC:	440 V

power dissipation at full load of the item:	4,2 W
tensión de pico Uimp:	6 kV
tensión máxima (IEC) AC:	1000 V
tensión máxima (IEC) DC:	1000 V
corriente de cortocircuito cuando se protege por fusibles:	50 kA

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contactos:
	spring-loaded copper contacts, silver plated 
Protección contra contacto:
	temperature stability 125°C,
	 self-extinguishing in acc. to UL 94,
	 creepage resistance CTI 600,
	 halogen-free 

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2.

Brand 
Woehner or equivalent

Part No.
03758000