Text for specification

Descripción
CAPUS^®Panel
interruptor-seccionador de 3 polos
tornillo M10, maneta roja
400 A

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB)

datos eléctricos
intensidad de corriente nominal (IEC):	400 A
tensión nominal (IEC) AC:	500 V

AC-23B (500V)
AC-22B (500V)
AC-21B (500V)

power dissipation at full load of the item:	57,0 W

tensión nominal de aislamiento Ui AC:	1000 V
tensión de pico Uimp:	12 kV
capacidad de cerrar a cortocircuito:	30 kA

Mechanical lifespan (switching operations) 7000
rated short-circuit making capacity 30kA

conv. therm. current in housing
400A, horizontal installation (adjacent poles) encapsulated 504 x 378 x 302mm
400A, vertical installation (poles beneath each other) encapsulated 500 x 500 x 300mm

Shock protection at front with terminal space cover IP40

puntos de apriete
Tornillo M10 :
Par de apriete 25 - 31 Nm

Miscellaneous 
double-breaking main contacts, visible separation sections, user-independent switching, assembly and connection material contained in scope of delivery

Brand 
Woehner or equivalent

Part No.
33356000