Text for specification

Descripción
QUADRON®60Classic
seccionador NH, talla 00, 160 A, montaje sobre barras, conexión superior / inferior
tornillo M8
60Classic

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB), UL, VDE, CCC

datos eléctricos
intensidad de corriente nominal (IEC):	160 A
tensión nominal (IEC) AC:	690 V
tensión nominal (IEC) DC:	440 V

intensidad de corriente nominal (UL):	160 A
tensión nominal (UL) AC:	600 V

AC-21B (690V)
AC-22B (500V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-21B (220V)
DC-21B (440V/100A)
DC-22B (220V/63A)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

power dissipation at full load of the item:	17,7 W

tensión nominal de aislamiento Ui AC:	800 V
tensión de pico Uimp:	6 kV
tensión máxima (IEC) DC:	800 V

SCCR:	100 kA

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protección contra contacto:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94, 
	Resistencia a las corrientes de fuga CTI 200
Tapa:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94, 
	Resistencia a las corrientes de fuga CTI 200
Placa adaptadora:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contactos:
	spring-loaded copper contacts, silver plated 
Tornillos de conexión:
	screw M8, galvanized, chromized

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into 2
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Part No.
33398000