Text for specification

Descripción
SECUR®60Classic EasyLiner
D0 interruptor-seccionador con fusibles, para embarrado de 3 polos
para los fusibles D01 y D02
E 18/63 A/3P
60Classic

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB), VDE, CCC

datos eléctricos
intensidad de corriente nominal (IEC):	63 A
tensión nominal (IEC) AC:	400 V

AC-22B (400 V)

power dissipation at full load of the item:	7,0 W

tensión nominal de aislamiento Ui AC:	500 V
tensión de pico Uimp:	6 kV

reduction factor at ambient temperature:
35°C     1,0
45°C     0,9
55°C     0,8

for fuse links and gauge elements acc. to IEC / HD 60269-3

use of D02 fuse links with silver plated caps is recommended

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

puntos de apriete
1,5 - 16 mm² round stranded and flexible without wire-end ferrule
1,5 - 16 mm²  flexible with wire-end ferrule*
1,5 - 10 mm²  flexible with wire-end ferrule
1,5 - 10 mm² round solid

* 16 mm² prepared with crimping tool PZ 16 (Weidmüller) or
with jointing clamp Crimpfox 25R (Phoenix Contact)

the connecting wires can be placed at the side : 
up to 6mm² without side module
up to 10mm² when using  the side module

cualidad de materiales
Caja:
	temperature stability 130°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free 
Palanca:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
spring terminal enables connection without tools (at first installation)

Brand 
Woehner or equivalent

Part No.
31574000B