Text for specification

Descripción
soporte para barras de conexión
3 polos, con bornes integrados de 1,5 a 16 mm²
60Classic

Normas
IEC 61439-1:2011

datos eléctricos
intensidad de corriente nominal (IEC):	63 A
tensión nominal (IEC) AC:	690 V

power dissipation at full load of the item:	0,8 W
máxima intensidad de corriente (IEC):	80 A

tensión nominal de aislamiento Ui AC:	800 V
tensión de pico Uimp:	6 kV

Current capacity of the clamping point 80A
short-circuit withstand rating:
surge current strength &gt; 30kA at busbar support separation of 550mm
surge current strength &gt; 50kA at busbar support separation of 250mm
further values in the short-circuit withstand rating diagram

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Tornillos:
	screw +/- (PZ2), galvanized, chromized 
Tapa:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94,
	Resistencia a las corrientes de fuga CTI 600

Miscellaneous 
Connection busbar support with integrated terminals for feeding or tapping the busbar
with internal screw holes, can also be used as centre support.

Brand 
Woehner or equivalent

Part No.
01484000