Text for specification

Descripción
SECUR^®60Classic PowerLiner
D0 interruptor-seccionador con fusibles sobre barras
para los fusibles D01 y D02
E 18/63 A/3P
60Classic

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
VDE, CCC

datos eléctricos
intensidad de corriente nominal (IEC):	63 A
tensión nominal (IEC) AC:	400 V
tensión nominal (IEC) DC:	110 V

AC-23A (400 V)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

power dissipation at full load of the item:	10,5 W

tensión nominal de aislamiento Ui AC:	500 V
tensión de pico Uimp:	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

puntos de apriete
frame terminal:
Cu 1,5 - 6 mm² round solid
Cu 1,5 - 16 mm² flexible with or without ferrule

cualidad de materiales
Caja:
	Resistencia a la temperatura hasta 140°C,
	autoextintor según UL 94, 
	Resistencia a las corrientes de fuga CTI 225,
	Sin silicona, sin halógenos
Palanca:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Soporte de fusibles:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Cubierta:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Tornillos de conexión:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Part No.
31158000