Text for specification

Descripción
AMBUS®Panel
soporte para fusibles cilíndricos
Class J / 3P, borne-brida 50 mm²
60 A / 600 V (27x60)

Normas
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

homologaciónes
CSA, UL

datos eléctricos

intensidad de corriente nominal (UL):	60 A
tensión nominal (UL) AC:	600 V
tensión nominal (UL) DC:	600 V

power dissipation at full load of the item:	3,9 W

SCCR:	200 kA

for Class J fuses 35 - 60A as per UL 248-8 (27x60)

puntos de apriete
for applications acc. to IEC / EN :
1 wire : Cu 6 - 50 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of same cross-section) : Cu 6 - 16 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire : AWG 14 - AWG 1, Class C, Md 4,0 Nm / 35 lb.in.
2 wires (of identical cross-section) :  AWG 14 - AWG 6, Class C, Md 4,0 Nm / 35 lb.in.

cualidad de materiales
Cuerpo principal:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Soporte de fusibles:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Tornillos de conexión:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label

Brand 
Woehner or equivalent

Part No.
31922000