Text for specification

Descripción
interruptor-seccionador fusible vertical, 160 A
tornillo M8/brida de 70mm²
talla 00
100Energy
185mm-System

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB), CCC

datos eléctricos
intensidad de corriente nominal (IEC):	160 A
tensión nominal (IEC) AC:	800 V

AC22 B (690 V) 
AC23 B (400V)
AC23 B (500V / 125A) AC20 (800 V) Sichtbarer Hinweis notwendig: Nicht unter Last schalten in Fall von Betriebsspannung höher als 690 V   

DC-20B
max. voltage between the fuses: 1000V
visible information required: Do not switch under load.

power dissipation at full load of the item:	20,0 W

tensión nominal de aislamiento Ui AC:	1000 V
tensión de pico Uimp:	8 kV
tensión máxima (IEC) DC:	1000 V

Degree of protection IP30 at front, degree of protection near terminal depends on installation

puntos de apriete
Tornillo M8 : 
Par de apriete 12 - 14 Nm

cualidad de materiales
Cuerpo principal:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94, 
	Resistencia a las corrientes de fuga CTI 200
Contactos:
	spring-loaded copper contacts, silver plated 
Protección contra contacto:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Tapa:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Part No.
33235000