Text for specification

Descripción
interruptor-seccionador fusible vertical, 160 A
tornillo M8/brida de 70mm², con control electr. de fusibles
talla 00
100Energy
185mm-System

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
IEC (CB), CCC

datos eléctricos
intensidad de corriente nominal (IEC):	160 A
tensión nominal (IEC) AC:	400 V

AC-23B (400V)

power dissipation at full load of the item:	20,0 W

tensión nominal de aislamiento Ui AC:	400 V
tensión de pico Uimp:	4 kV

Electronic fuse monitoring:
nominal voltage: 3AC 400V,
nominal frequency: 50...40Hz,
switch contact: 2 changeover switches, max. AC 250V, AC15  closer 3A, opener 1A,
rated surge voltage: 4kV,
pollution degree: 2

Degree of protection IP30 at front, degree of protection near terminal depends on installation

puntos de apriete
Tornillo M8 : 
Par de apriete 12 - 14 Nm

cualidad de materiales
Cuerpo principal:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94, 
	Resistencia a las corrientes de fuga CTI 200
Contactos:
	spring-loaded copper contacts, silver plated 
Protección contra contacto:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Tapa:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
Self-closing inspection holes are available in the cover.
Electronic fuse monitoring:
operating current principle, optionally with latching properties (latches without bridge X1-X2)
device display:
green LED = intact fuses
red LED = fuse tripped, cover position up

Brand 
Woehner or equivalent

Part No.
33286000