Text for specification

Descripción
QUADRON®60Classic
seccionador-interruptor con fusibles NH talla 000, 125 A
borne brida
adecuado para instalación de 5 polos
60Classic

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

datos eléctricos
intensidad de corriente nominal (IEC):	125 A
tensión nominal (IEC) AC:	690 V
tensión nominal (IEC) DC:	440 V

AC-21B (690 V / 80 A)
AC-22B (400 V / 125 A)

power dissipation at full load of the item:	10,5 W

tensión nominal de aislamiento Ui AC:	800 V
tensión de pico Uimp:	6 kV
tensión máxima (IEC) DC:	800 V

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

puntos de apriete
box terminal:
1.5 - 50 mm² flexible and flexible with wire-end ferrules*
2.5 - 50 mm² flexible
2.5 - 16 mm² solid round
2.5 - 50 mm² stranded round

Terminal space 10 mm x 10 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

cualidad de materiales
Caja:
	temperature stability 125°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free
Tapa:
	Resistencia a la temperatura hasta 125°C, 
	autoextintor según UL 94,
	Resistencia a las corrientes de fuga CTI 600
Contactos:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
only 49.5 mm wide rotatable for connection at bottom or top 

Brand 
Woehner or equivalent

Part No.
33803000A