Text for specification

Descripción
QUADRON^®60Classic Speed
seccionador con fusibles, 3 polos
borne-brida, conexión inferior, para acoplamiento a puerta
talla 00
60Classic

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

datos eléctricos
intensidad de corriente nominal (IEC):	125 A
tensión nominal (IEC) AC:	690 V

AC-23B (690V/125A)
AC-23A (500V/125A)
AC-22A (690V/125A)

AC20B (800V)
visible information required: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V/125A)

DC-20B (800V) at pollution degree 3
visible information required: do not switch under load

tensión nominal de aislamiento Ui AC:	800 V
tensión de pico Uimp:	8 kV

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, degree of protection near terminal depends on installation; shock protection as per DIN EN 50274

adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

puntos de apriete
Box terminal:
1.5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable 
1.5 - 10mm² solid round
16 - 70mm² stranded round 
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x10 - 2x35mm² flexible, identical cables placed side by side square

lam. Cu. 9-13 mm wide 
Terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category "A"
FLAG indicator shows the switch setting
Fuses can be changed safely and without tools thanks to double-breaking main contacts
Additional visible separating section by removing the cover incl. fuses
Can be used as mains disconnector as per IEC / EN 60204-1 (main switch)
Also as an Emergency Off switch in combination with the red-yellow door coupling twist handle
Main switch and Emergency Off switch only in combination with AC-23A/B

CrossLink® adapter technology
Simple and safe clicking into place and making contact
Busbar supports can be mounted above each other for flat busbars
Compact dimensions (106mm wide)

Switches can be installed 90° left/right horizontal, always with the same switch lug position

Brand 
Woehner or equivalent

Part No.
33503000