Text for specification

Descripción
QUADRON^®Panel Speed
seccionador con fusibles, 3 polos
borne-brida, con control electrónico de fusión
talla 00

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

datos eléctricos
intensidad de corriente nominal (IEC):	125 A
tensión nominal (IEC) AC:	690 V

AC-23B (690V/125A)
AC-23A (500V/125A)
AC-22A (690V/125A)   

2 current paths (L1,L3) in series
DC-22B (220V/125A)

tensión nominal de aislamiento Ui AC:	690 V
tensión de pico Uimp:	6 kV
tensión máxima (IEC) AC:	725 V

utilisation categories AC-23B (690V/125A), AC-23A (500V/125A), AC-22A (690V/125A), DC-22B (220V/125A), 2 current paths (L1,L3) in series; fuses gL/gG, size 00, 690V/125A for fuse links IEC 60269-2 / DIN VDE 0636-2 size 00 up to 10W power dissipation,

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.
Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

System component: degree of protection IP20 at front as per DIN EN 60529, dependent upon installation in the connection area; shock protection to DIN EN 50274

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

puntos de apriete
Box terminal:
1.5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable 
1.5 - 10mm² solid round
16 - 70mm² stranded round 
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x10 - 2x35mm² flexible, identical cables placed side by side square

lam. Cu. 9-13 mm wide 
Terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category &quot;A&quot;
Can be locked in neutral position with up to 3 padlocks
FLAG indicator shows the switch setting
Fuses can be changed safely and without tools thanks to double-breaking main contacts
Additional visible separating section by removing the cover incl. fuses
Can be used as a mains disconnector as per IEC/EN 60204-1 (main switch)
Main switch only in combination with AC-23A/B

Brand 
Woehner or equivalent

Part No.
33507000