Text for specification

Descripción
QUADRON®185Power
base vertical para fusibles NH, 630 A
tornillo M12
talla 3
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Normas
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

datos eléctricos
intensidad de corriente nominal (IEC):	630 A
tensión nominal (IEC) AC:	690 V
tensión de pico Uimp:	12 kV
tensión máxima (IEC) AC:	1000 V
corriente de cortocircuito cuando se protege por fusibles:	50 kA

for fuse links IEC 60269-2 / DIN VDE 0636-201 size 3 up to 48W power dissipation 

puntos de apriete
screw M12 :
Md 30 Nm

Brand 
Woehner or equivalent

Part No.
33708000A