Text for specification

Descripción
SECUR^®Panel
seccionador para fusibles D0 de hasta 25 A
3P

Normas
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

homologaciónes
VDE, CCC

datos eléctricos
intensidad de corriente nominal (IEC):	25 A
tensión nominal (IEC) AC:	400 V
tensión nominal (IEC) DC:	130 V

power dissipation at full load of the item:	7,8 W

tensión nominal de aislamiento Ui AC:	500 V
tensión de pico Uimp:	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

puntos de apriete
box terminal :
1,5 - 35 mm²    flexible cables, directly or with wire-end ferrule
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
1,5 - 10 mm²    solid
Md 2,5 - 3 Nm

2 cables can be connected, when both chambers of the terminal are used
the maximum combination is 35mm² + 16mm²

cualidad de materiales
Caja:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Palanca:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Soporte de fusibles:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Tornillos de conexión:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Part No.
31532000A