Text for specification

Désignation
EQUES^®185Power
adaptatateur pour système base 2x 160 A
pour des produits CrossBoard®
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Normes
IEC 61439-1:2011

Approbations
UL

Charactéristiques électriques
Courant assigné (IEC):	320 A
Tension assignée (IEC) CA:	690 V

rated current (UL):	320 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	48,6 W

rated isolation voltage U_i AC:	1000 V
Tension assignée de tenue aux chocs Uimp:	6 kV

SCCR: 35 kA with any DIVQ/7 circuit breaker 125 A / 600 V AC, 65 kA with any DIVQ/7 circuit breaker 125 A / 480 V AC 

Observe the important instructions regarding short-circuit capacity when using CrossBoard® components

When used with 4x NH switch-disconnector size 000 (Part No. 33800) and direct cable connections provided by the customer without a terminal block, the following current capacities have been verified by tests:

with fuses 63 A / 500 V (AC) and cable connection 25 mm²: 4x 63 A
with fuses 80 A / 690 V (AC) and cable connection 25 mm²: 4x 68 A
with fuses 100 A / 500 V (AC) and cable connection 35 mm²: 4x 80 A

Brand 
Woehner or equivalent

Référence
32277000A