Text for specification

Désignation
QUADRON®60Classic Speed
sectionneur avec fusibles à 3 pôles
vis M10, raccordement par le bas, pour poignée rotative de couplage de porte
taille 1
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), VDE

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	690 V

AC-23B (690V/250A)
AC-23A (500V/250A)
AC-22A (690V/250A)

AC20B (800V)
pollution degree 3, visible information required: do not switch under load

DC-20B (800 V)
pollution degree 3, visible information required: do not switch under load

power dissipation at full load of the item:	82,0 W

rated isolation voltage Ui AC:	800 V
Tension assignée de tenue aux chocs Uimp:	8 kV

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, degree of protection near terminal depends on installation; shock protection as per DIN EN 50274

adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Platine adaptateur:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Couvercle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Vis de raccordement:
	screw M10, galvanized, chromized

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category "A"
FLAG indicator shows the switch setting
Fuses can be changed safely and without tools thanks to double-breaking main contacts
Additional visible separating section by removing the cover incl. fuses
Can be used as mains disconnector as per IEC / EN 60204-1 (main switch)
Also as an Emergency Off switch in combination with the red-yellow door coupling twist handle

CrossLink® adapter technology
Simple and safe clicking into place and making contact
Busbar supports can be mounted above each other for flat busbars

Switched can be installed 90° left/right horizontal, always with the same switch lug position

Brand 
Woehner or equivalent

Référence
33513000