Text for specification

Désignation
QUADRON^®60Classic
fusible-interrupteur-sectionneur NH taille 000, 125 A
borne à cage
convient pour un système à 5 pôles
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Charactéristiques électriques
Courant assigné (IEC):	125 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

AC-21B (690 V / 80 A)
AC-22B (400 V / 125 A)

power dissipation at full load of the item:	10,5 W

rated isolation voltage U_i AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CC:	800 V

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

Points de raccordement
box terminal:
1.5 - 50 mm² flexible and flexible with wire-end ferrules*
2.5 - 50 mm² flexible
2.5 - 16 mm² solid round
2.5 - 50 mm² stranded round

Terminal space 10 mm x 10 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Charactéristiques des matériaux
Boîtier:
	temperature stability 125°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free
Couvercle:
	tenue en température 125°C, 
	auto-extinguible conf. à l'UL 94,
	tenue au courant de fuite CTI 600
Contacts:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
only 49.5 mm wide rotatable for connection at bottom or top 

Brand 
Woehner or equivalent

Référence
33803000A