Text for specification

Désignation
SECUR®60Classic EasyLiner
interrupteur-sectionneur à fusibles D0, pour jeu de barres 3 pôles
pour fusibles D01 et D02, avec LED
E18 / 63 A / 3P
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	63 A
Tension assignée (IEC) CA:	400 V

AC-22B (400 V)

power dissipation at full load of the item:	7,0 W

rated isolation voltage Ui AC:	500 V
Tension assignée de tenue aux chocs Uimp:	6 kV

reduction factor at ambient temperature:
 35°C     1,0
 45°C     0,9
 55°C     0,8

for fuse links and gauge elements acc. to IEC / HD 60269-3

 use of D02 fuse links with silver plated caps is recommended

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Points de raccordement
1,5 - 16 mm² round stranded and flexible without wire-end ferrule
1,5 - 16 mm²  flexible with wire-end ferrule*
1,5 - 10 mm²  flexible with wire-end ferrule
1,5 - 10 mm² round solid

* 16 mm² prepared with crimping tool PZ 16 (Weidmüller) or
with jointing clamp Crimpfox 25R (Phoenix Contact)

the connecting wires can be placed at the side :
up to 6mm² without side module
up to 10mm² when using  the side module

Miscellaneous 
spring terminal enables connection without tools (at first installation)

Brand 
Woehner or equivalent

Référence
31575000B