Text for specification

Désignation
QUADRON^®Panel
sectionneur à fusible NH taille 00, 160 A, à encastrer
vis M8

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	160 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	250 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-23B (400 V)
AC-23B (500 V / 125A)
AC-22B (690 V)
AC-21B (690 V)

DC specifications: 2 current paths (L1,L3) in series
DC-22B (250V)

power dissipation at full load of the item:	7,0 W

rated isolation voltage U_i AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	725 V
Tension maximale IEC CC:	262 V

Icc:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 00 up to 12W power dissipation, with grip lugs under voltage

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich

Degree of protection IP30 at front, degree of protection near terminal depends on installation
fuse monitoring:
rated operating voltage
AC 24-690V, DC 24-250V
potential-free opener and closer:
AC-15 24V/2A, (230V* 0.5A)
DC-13 24V/1A, 60V 0.15A

*pollution degree 2, surge category II
auxiliary energy not required,
for further information, see assembly manual

Points de raccordement
Accessories:
Clamp connection:  Cu 1.5-70mm² s(r), f+AE; lam. Cu 12x1-10; 3Nm torque
single wedge clamp terminal: Cu, Al* 16-70mm² s(r), s(s), f+AE; 3Nm torque
tunnel terminal 3x Cu 1.5-16mm² s(r), f+AE; 3Nm torque

*Connections not maintenance-free if aluminium conductors are used.

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2.

Brand 
Woehner or equivalent

Référence
33208000