Text for specification

Désignation
QUADRON 60Classic
sectionneur à fusible NH taille 1, 250 A
vis M10
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

rated current (UL):	250 A
rated voltage (UL) AC:	600 V

AC-21B (690 V / 250A)
AC-22B (400 V / 250A)

DC specifications: 2 current paths (L1,L3) in series
DC-20B (440 V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

power dissipation at full load of the item:	26,0 W

rated isolation voltage Ui AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	725 V
Tension maximale IEC CC:	800 V

rated peak withstand current  Ipk max.:	13,7 kA

Icc:	100 kA

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other
Self-closing test holes are available in the cover.

Brand 
Woehner or equivalent

Référence
33601000