Text for specification

Désignation
QUADRON®185Power
module comprenant 4 x NH inter sectionneur à fusible, tripolaire
4x NH 000 (max. 63 A)
185Power

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Charactéristiques électriques
Courant assigné (IEC):	252 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

AC-21B (690 V / 80 A)
AC-22B (400 V / 125 A)

power dissipation at full load of the item:	103,0 W

rated isolation voltage Ui AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV

The following current capacities have been verified by tests:

with fuses 63 A / 500 V (AC): 4x 63 A
with fuses 80 A / 690 V (AC): 4x 68 A

Points de raccordement
tunnel terminal 1.5 - 50 mm²

Cu: 1.5 - 50 mm² flexible with wire-end ferrule
Cu: 16 - 50 mm² stranded round
Cu: 1.5 - 10 mm² solid round

Al: 16 - 50 mm² solid round
Al: 50 mm² stranded sectored, pre-rounded 

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Référence
33778000A