Text for specification

Désignation
SECUR^®60Classic PowerLiner
interrupteur-sectionneur à fusibles D0 pour jeu de barres
pour fusibles 10x38 IEC 60269-2
3P
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Charactéristiques électriques
Courant assigné (IEC):	32 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	110 V

AC-23A (400 V)
AC-22A (690 V) 

power dissipation at full load of the item:	5,3 W

rated isolation voltage U_i AC:	500 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	725 V

for fuse links gG and aM as per IEC / EN 60269-2

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Charactéristiques des matériaux
Boîtier:
	tenue en température 140°C,
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 225,
	sans silicone, sans halogéne
Levier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Tiroir fusible:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Vis de raccordement:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Référence
31232000