Text for specification

Désignation
CRITO^®60Classic
plaque bornier, 3 pôles
10 - 120 mm², AWG 2 - 250 MCM, lam. Cu. 9 - 15,5 x 2,4 - 10
le cache peut uniquement être retiré à l'aide d'un outil
60Classic

Normes
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approbations
CSA, UL

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	690 V

rated current (UL):	255 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	440 A
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	1000 V
Tension maximale IEC CC:	1500 V

rated peak withstand current  I_pk max.:	56,3 kA

SCCR: 100 kA with JDDZ fuse Class J 600 A / 480 V AC, 35 kA with any DIVQ/7 circuit breaker 600 A / 600 V AC, 100 kA with JDDZ fuse Class J 500 A / 600 V AC, 50 kA with any DIVQ/7 circuit breaker 600 A / 480 V AC, 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC 

Points de raccordement
16 - 120 mm² / AWG 6 - 250 MCM flexible cables, directly
10 - 120 mm² / AWG 7 - 250 MCM flexible cables with wire-end ferrule
16 - 150 mm² / AWG 6 - 300 MCM stranded round cables
10 mm² rigid cables
lam. Cu 12x4 - 15,5x10
Md 12 - 12,5 Nm / 106 lb-in

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free

Miscellaneous 
Terminals can be removed for connection of uncut conductors

Brand 
Woehner or equivalent

Référence
01570000A