Text for specification

Désignation
QUADRON®Panel
embase de fusible NH 250 A, à encastrer, pour PV
vis de raccordement M10 pour borne d'arrivée, borne de départ au jeu de barres 2x 30 x 10, pour intégration TC, modèles LEM HTA
taille 1XL / 1P, avec protection contre les contacts

Normes
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	1000 V
Tension assignée (IEC) CC:	1500 V

power dissipation at full load of the item:	5,5 W
Tension assignée de tenue aux chocs Uimp:	6 kV
short-circuit strength when protected by fuses:	50 kA

for fuse links IEC 60269-6

Points de raccordement
Connection screws for busbars: Hexagonal screw M10, length across flats 16, tightening torque 30Nm
connection width 25mm 
fastening to mounting plate: 2x 10.5mm hole, intended for hexagonal screw M10, tightening torque 5Nm

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Vis de raccordement:
	screw M10, galvanized, chromized
Protection contre les contacts directs:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
For one or two internal busbars 30x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Référence
03288000