Text for specification

Désignation
réglette sectionneur à fusible 160 A
vis M8 / collier 70mm²
taille 00
100Energy
185mm-System

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), CCC

Charactéristiques électriques
Courant assigné (IEC):	160 A
Tension assignée (IEC) CA:	800 V

AC22 B (690 V) 
AC23 B (400V)
AC23 B (500V / 125A) AC20 (800 V) Sichtbarer Hinweis notwendig: Nicht unter Last schalten in Fall von Betriebsspannung höher als 690 V   

DC-20B
max. voltage between the fuses: 1000V
visible information required: Do not switch under load.

power dissipation at full load of the item:	20,0 W

rated isolation voltage Ui AC:	1000 V
Tension assignée de tenue aux chocs Uimp:	8 kV
Tension maximale IEC CC:	1000 V

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Points de raccordement
vis M8 : 
Md 12 - 14 Nm

Charactéristiques des matériaux
Embase:
	tenue en température 125°C, 
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 200
Contacts:
	spring-loaded copper contacts, silver plated 
Protection contre les contacts directs:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Couvercle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Référence
33235000