Text for specification

Désignation
QUADRON^®60Classic
sectionneur à fusible NH taille 1, 250 A, montage sur rail, raccordement par le haut / par le bas
vis M10
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	250 V

rated current (UL):	250 A
rated voltage (UL) AC:	600 V

AC-22B (400 V)
AC-23B (400 V / 160 A)
AC-21B (500 V)

to obtain a higher utilisation category the product can be retrofitted with arcing chambers (see accessories)

power dissipation at full load of the item:	26,0 W

rated isolation voltage U_i AC:	690 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	725 V
Tension maximale IEC CC:	262 V

rated peak withstand current  I_pk max.:	13,7 kA

Icc:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 1 up to 23W power dissipation, with grip lugs under voltage

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Schutzart IP30 frontseitig, im Anschlussbereich vom Einbau abhängig

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protection contre les contacts directs:
	tenue en température 125°C, 
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 200
Couvercle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Platine adaptateur:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Vis de raccordement:
	screw M10, galvanized, chromized

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other
Self-closing test holes are available in the cover.

Brand 
Woehner or equivalent

Référence
33325000