Text for specification

Désignation
QUADRON^®Panel
sectionneur à fusible NH taille 2, 400 A, à encastrer
vis M10

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	400 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	250 V

rated current (UL):	400 A
rated voltage (UL) AC:	600 V

AC-23B (400V)
AC-22B (500 V)
AC-21B (500 V)

power dissipation at full load of the item:	22,0 W

rated isolation voltage U_i AC:	690 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	725 V
Tension maximale IEC CC:	262 V

Icc:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 2 up to 34W power dissipation, with grip lugs under voltage

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Schutzart IP30 frontseitig, im Anschlussbereich vom Einbau abhängig

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

Points de raccordement
Accessories:
Clamp connection:  Cu 120-240mm² s(r), f+AE; lam. Cu 21x1-14; 6-8Nm torque
single wedge clamp terminal: Cu, Al* 120-240mm² s(r), s(s), f, f+AE; 6-8 Nm torque
double wedge clamp terminal: Cu  2x 70-120mm² s(r), s(s), f+AE;  6-8Nm torque

*Connections are not maintenance-free if aluminium conductors are used.

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protection contre les contacts directs:
	tenue en température 125°C, 
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 200
Couvercle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
For safe connection of the lines, the shock protection is split into 2.
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Référence
33331000