Text for specification

Désignation
QUADRON®30Compact
fusible-interrupteur-sectionneur NH taille 000, 125 A, pour jeu de barres, raccordement par le haut / bas
borne à cage
30Compact 3P

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	125 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

rated current (UL):	125 A
rated voltage (UL) AC:	600 V

AC-23B (400 V)
AC-22B (500 V)
AC-21B (690 V)

DC specifications: 2 current paths (L1,L3) in series 
DC-22B (440V/63A)
DC-22B (220V/100A)
DC-21B (440V/80A)
DC-21B (220V/125A)

power dissipation at full load of the item:	13,8 W

rated isolation voltage Ui AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CC:	800 V

Icc:	100 kA

for fuse links IEC 60269-2 / DIN VDE 0636-2 size 000 (max. 21mm wide) up to 9W power dissipation

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Bei Dauerbetrieb von mehreren Geräten nebeneinander ist der Bemessungsbelastungsfaktor nach VDE 0660 Teil 500 / EN60439-1, Tabelle 1 zu beachten.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation, adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Points de raccordement
Box terminal:
2.5 -50mm² flexible cables, 
1.5 -50mm² flexible cables with wire-end ferrules 
1.5 - 10mm² solid round
16 - 50mm² stranded round 
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
lam. Cu. 6-9 mm wide 
Terminal space 10mm x 10mm

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Protection contre les contacts directs:
	tenue en température 125°C, 
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 200
Couvercle:
	tenue en température 125°C, 
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 200
Platine adaptateur:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected 
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two

Brand 
Woehner or equivalent

Référence
33416000