Text for specification

Désignation
QUADRON^®Panel
embase de fusible NH 250 A, à encastrer, pour PV
vis de raccordement M10 pour borne d'arrivée, borne de départ au jeu de barres 2x 30 x 10, pour intégration TC, modèles LEM HTA
taille 1XL / 1P, avec protection contre les contacts

Normes
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	1000 V
Tension assignée (IEC) CC:	1500 V

power dissipation at full load of the item:	5,5 W
Tension assignée de tenue aux chocs Uimp:	6 kV
short-circuit strength when protected by fuses:	50 kA

for fuse links IEC 60269-6

Points de raccordement
Connection screws for busbars: Hexagonal screw M10, length across flats 16, tightening torque 30Nm
connection width 25mm 
fastening to mounting plate: 2x 10.5mm hole, intended for hexagonal screw M10, tightening torque 5Nm

Miscellaneous 
For one or two internal busbars 30x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Référence
03288000