Text for specification

Désignation
QUADRON^®Panel
sectionneur à fusible NH taille 00, 160 A, à encastrer
étrier 70 mm²

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	160 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-23B (400V)
AC-23B (500V/125A)
AC-22B (690V)
AC-21B (690V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V)
DC-22B (440V/125A)
DC-21B (440V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

power dissipation at full load of the item:	7,0 W

rated isolation voltage U_i AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CC:	800 V

Icc:	100 kA

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Points de raccordement
bornes à étrier : 
1,5 - 70 mm² 
câble souple avec embout, 
câble rond multi-brins, 
la. Cu larg. max. 12 mm, épaiss. max. 10 mm
Md 3 Nm

(câble souple de section maxi ne convient pas si équipé d'embout)

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2. Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Référence
33199000