Text for specification

Désignation
QUADRON^®60Classic
sectionneur à fusible NH taille 00, 160 A, monté sur rail, raccordement par le haut / par le bas
borne à cage
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	160 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	250 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-21B (690V)
AC-22B (500V)

DC specifications: 2 current paths (L1,L3) in series
DC-21B (220V)
DC-22B (220V/63A)

power dissipation at full load of the item:	17,7 W

rated isolation voltage U_i AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	725 V
Tension maximale IEC CC:	262 V

Icc:	100 kA

for fuse links IEC 60269-2 / DIN VDE 0636-2 size 00 up to 12W power dissipation, with grip lugs under voltage

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Bei Dauerbetrieb von mehreren Geräten nebeneinander ist der Bemessungsbelastungsfaktor nach VDE 0660 Teil 500 / EN60439-1, Tabelle 1 zu beachten.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: degree of protection IP20 at front as per DIN EN 60529 (finger-safe)

Fuse monitoring:
rated operating voltage
AC 24-690V, DC 24-250V
potential-free opener and closer:
AC-15 24V/2A, (230V* 0.5A)
DC-13 24V/1A, 60V 0.15A

*pollution degree 2, surge category II
auxiliary energy not required,
for further information, see assembly manual

Points de raccordement
Box terminal:
1.5 - 70 mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the lead 95 mm² could be connectable 
1.5 - 10 mm² solid round
16 - 70 mm² stranded round 
2x 10 mm², 2x 16 mm² and 2x 25 mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x 10 - 35 mm² flexible identical cables placed side by side

lam. Cu. 9 - 13 mm wide 
terminal space 13 mm x 13 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

für Anwendungen nach UL :
  nur Cu-Leitungen stranded/solid nach UL 486E
  AWG 12 - AWG 2/0
  Md 5,0 - 6,0 Nm / 44 - 53 lb.in. 

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Référence
33206000