Text for specification

Désignation
QUADRON®60Classic
sectionneur à fusible NH taille 000, 125 A, monté sur rail, raccordement par le haut / par le bas
borne à cage
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	125 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

rated current (UL):	125 A
rated voltage (UL) AC:	600 V

AC-23B (400 V)
AC-22B (500 V)
AC-21B (690 V)

DC specifications: 2 current paths (L1,L3) in series 
DC-22B (440V/63A)
DC-22B (220V/100A)
DC-21B (440V/80A)
DC-21B (220V/125A)

power dissipation at full load of the item:	10,5 W

rated isolation voltage Ui AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CC:	800 V

Icc:	100 kA

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Points de raccordement
Box terminal:
2.5 -50mm² flexible cables, 
1.5 -50mm² flexible cables with wire-end ferrules 
1.5 - 10mm² solid round
16 - 50mm² stranded round 
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
lam. Cu. 6-9 mm wide 
Terminal space 10mm x 10mm

Miscellaneous 
Self-closing inspection holes are available in the cover.

Brand 
Woehner or equivalent

Référence
33216000