Text for specification

Désignation
AMBUS^®Panel
support pour fusibles cylindriques
10x38 / 2P
32 A / 690 V

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), CSA, UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	32 A
Tension assignée (IEC) CA:	690 V

rated current (UL):	30 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

AC-22B (400V)

power dissipation at full load of the item:	0,6 W

rated isolation voltage U_i AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV

Icc:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipations
up to max. 3W for gG/gL 
up to max. 1.2W for aM

Points de raccordement
for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section): 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Tiroir fusible:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Vis de raccordement:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range
holder for label

Brand 
Woehner or equivalent

Référence
31112000