Text for specification

Désignation
EQUES^®185Power
adaptateur de jeu de barres, 1250 A
300 x 652, connexion par le haut, contact de serrage 
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Normes
IEC 61439-1:2011

Approbations
UL

Charactéristiques électriques
Courant assigné (IEC):	1 250 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	800 V

rated current (UL):	1 200 A
rated voltage (UL) AC:	1000 V

power dissipation at full load of the item:	363,0 W

rated isolation voltage U_i AC:	1000 V
Tension assignée de tenue aux chocs Uimp:	12 kV

rated peak withstand current  I_pk max.:	106 kA

Brand 
Woehner or equivalent

Référence
32757000A