Text for specification

Désignation
QUADRON^®60Classic
sectionneur à fusible NH taille 00, 160 A, monté sur rail, raccordement par le haut / par le bas
borne à cage
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	160 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

rated current (UL):	160 A
rated voltage (UL) AC:	600 V

AC-21B (690 V)
AC-22B (500 V)

power dissipation at full load of the item:	17,7 W

rated isolation voltage U_i AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CC:	800 V

Icc:	100 kA

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Points de raccordement
Box terminal:
1.5 - 70 mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the lead 95 mm² could be connectable 
1.5 - 10 mm² solid round
16 - 70 mm² stranded round 
2x 10 mm², 2x 16 mm² and 2x 25 mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x 10 - 35 mm² flexible identical cables placed side by side

lam. Cu. 9 - 13 mm wide 
terminal space 13 mm x 13 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

for applications according UL :
Cu cables only, stranded/solid according UL 486E
AWG 12 - AWG 2/0
tightening torque 5,0 - 6,0 Nm / 44 - 53 lb.in.

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
If flat busbars are used the device can be mounted covering the busbar support

Brand 
Woehner or equivalent

Référence
33198000