Text for specification

Désignation
CRITO®60Classic
plaque bornier, 3 pôles
10 - 120 mm², AWG 2 - 250 MCM, lam. Cu. 9 - 15,5 x 2,4 - 10
le cache peut uniquement être retiré à l'aide d'un outil
60Classic

Normes
IEC 61439-1:2020
IEC 60999-1:1999
IEC 60999-2:2003

Approbations
CSA, UL

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	690 V

rated current (UL):	255 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	440 A
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	1000 V
Tension maximale IEC CC:	1500 V

rated peak withstand current  Ipk max.:	56,3 kA

SCCR: 100 kA with JDDZ fuse Class J 500 A / 600 V AC, 100 kA with JDDZ fuse Class J 600 A / 480 V AC, 35 kA with any DIVQ/7 circuit breaker 600 A / 600 V AC, 50 kA with any DIVQ/7 circuit breaker 600 A / 480 V AC, 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC 

Points de raccordement
cage clamp connection
wire stripping: 25 mm
min. cross-section: 10 mm²
max. cross-section: 150 mm²
cage clamp connection
wire stripping: 25 mm
min. cross-section: 10 mm²
max. cross-section: 150 mm²
re: 10 - 10 mm²
rm: 16 - 150 mm²
f: 16 - 120 mm²
f + AE: 10 - 120 mm²
(f + AE may not fit with max. cross-section) 
Alvéole de serrage: 15 x 15 
Md min.: 12,0 Nm
Md max.: 12,5 Nm
Not suitable for aluminium cables !

Miscellaneous 
Terminals can be removed for connection of uncut conductors

Brand 
Woehner or equivalent

Référence
01570000A