Text for specification

Désignation
CRITO®
bornes à pince
Cu / Al 95 - 300 mm²
60Classic
100Energy
185mm-System
centre feed unit

Normes
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Approbations
CSA, UL

Charactéristiques électriques
Courant assigné (IEC):	500 A
Tension assignée (IEC) CA:	690 V

rated current (UL):	420 A
rated voltage (UL) AC:	600 V
current capacity (IEC) max.:	600 A
Tension maximale IEC CA:	1000 V
Tension maximale IEC CC:	1500 V

rated peak withstand current  Ipk max.:	81,4 kA

Icc:	65 kA

Points de raccordement
for applications acc. to IEC / EN :
Cu 95 - 300 mm² stranded round cables and stranded sectored cables as well as flexible cables (directly)
Cu 240 - 300 mm² fine stranded flexible cables (directly)
Al 120 - 300 mm² stranded round cables and stranded sectored cables
Al 120 - 240 mm² solid sectored cables

for applications acc. to UL / CSA :
Cu 95 - 300 mm² / AWG 3/0 - MCM 600

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Charactéristiques des matériaux
Vis de raccordement:
	Set screw M16, Allan key size 8
Corps de borne:
	steel, galvanized and chromized
cable base:
	brass, tin plated

Brand 
Woehner or equivalent

Référence
01760000