Text for specification

Désignation
QUADRON®Panel
embase de fusible NH 600 A, à encastrer, pour PV 
vis de raccordement M10 pour borne d'arrivée, borne de départ au jeu de barres 2x 40 x 10
taille 2XL / 3L, 1P, avec protection contre les contacts

Normes
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Charactéristiques électriques
Courant assigné (IEC):	600 A
Tension assignée (IEC) CA:	1000 V
Tension assignée (IEC) CC:	1500 V

rated current (UL):	600 A
rated voltage (UL) DC:	1500 V

power dissipation at full load of the item:	13,8 W
Tension assignée de tenue aux chocs Uimp:	6 kV
short-circuit strength when protected by fuses:	50 kA

Icc:	15 kA

Bei praxisgerechter Anordnung muss bezüglich Strombelastbarkeit, bezogen auf den Nennstrom der Sicherung, ein Reduktionsfaktor von 0,6 berücksichtigt werden.

for fuse links IEC 60269-6

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Vis de raccordement:
	screw M10, galvanized, chromized
Protection contre les contacts directs:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
For one or two internal busbars 40x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Référence
03293000