Text for specification

Désignation
QUADRON^®60Classic
embase de fusible NH 250 A
vis M10
taille 1 / 3P
60Classic

Normes
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Approbations
CCC

Charactéristiques électriques
Courant assigné (IEC):	250 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

power dissipation at full load of the item:	31,4 W
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	800 V
Tension maximale IEC CC:	800 V
short-circuit strength when protected by fuses:	80 kA

Adapter module, degree of protection IP20 at front

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Protection contre les contacts directs:
	tenue en température 125°C, 
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 200

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Référence
03301000