Text for specification

Désignation
QUADRON®Panel
embase de fusible NH 160 A
raccordement par étrié des 2 côtés
taille 00 / 1P, avec protection contre les contacts

Normes
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Charactéristiques électriques
Courant assigné (IEC):	160 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	440 V

power dissipation at full load of the item:	4,2 W
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	1000 V
Tension maximale IEC CC:	1000 V
short-circuit strength when protected by fuses:	50 kA

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Protection contre les contacts directs:
	temperature stability 125°C,
	 self-extinguishing in acc. to UL 94,
	 creepage resistance CTI 600,
	 halogen-free 

Miscellaneous 
For safe connection of the leads, the shock protection is split into 2.

Brand 
Woehner or equivalent

Référence
03758000