Text for specification

Désignation
SECUR®60Classic PowerLiner
interrupteur-sectionneur à fusibles D0 pour jeu de barres
pour fusibles D01 et D02
E18 / 63 A / 3P
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	63 A
Tension assignée (IEC) CA:	400 V
Tension assignée (IEC) CC:	110 V

AC-23A (400 V)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

power dissipation at full load of the item:	10,5 W

rated isolation voltage Ui AC:	500 V
Tension assignée de tenue aux chocs Uimp:	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Points de raccordement
frame terminal:
Cu 1,5 - 6 mm² round solid
Cu 1,5 - 16 mm² flexible with or without ferrule

Charactéristiques des matériaux
Boîtier:
	tenue en température 140°C,
	auto-extinguible conf. à l'UL 94, 
	tenue au courant de fuite CTI 225,
	sans silicone, sans halogéne
Levier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Tiroir fusible:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Vis de raccordement:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Référence
31158000