Text for specification

Désignation
AMBUS^®Panel
support pour fusibles cylindriques avec LED
Class J / 2P, borne à cage 50 mm²
60 A / 600 V (27x60)

Normes
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Approbations
CSA, UL

Charactéristiques électriques

rated current (UL):	60 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	2,6 W

Icc:	200 kA

for Class J fuses 35 - 60A as per UL 248-8 (27x60)

indicator light
operating voltage range: 110 - 600 V AC / DC

Points de raccordement
for applications acc. to IEC / EN :
1 wire : Cu 6 - 50 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of same cross-section) : Cu 6 - 16 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire : AWG 14 - AWG 1, Class C, Md 4,0 Nm / 35 lb.in.
2 wires (of identical cross-section) :  AWG 14 - AWG 6, Class C, Md 4,0 Nm / 35 lb.in.

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Tiroir fusible:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Vis de raccordement:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label
with indicator for tripped fuse
any polarity for DC voltage applications

Brand 
Woehner or equivalent

Référence
31924000