Text for specification

Désignation
QUADRON^®60Classic
sectionneur à fusible NH taille 2, 400 A, montage sur rail, raccordement par le haut / par le bas
vis M10
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	400 A
Tension assignée (IEC) CA:	690 V
Tension assignée (IEC) CC:	250 V

rated current (UL):	400 A
rated voltage (UL) AC:	600 V

AC-23B (400V)
AC-22B (500 V)
AC-21B (500 V)

power dissipation at full load of the item:	45,0 W

rated isolation voltage U_i AC:	690 V
Tension assignée de tenue aux chocs Uimp:	6 kV
Tension maximale IEC CA:	725 V
Tension maximale IEC CC:	262 V

Icc:	100 kA

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 2 up to 34W power dissipation, with grip lugs under voltage

Schutzart IP30 frontseitig, im Anschlussbereich vom Einbau abhängig

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

Points de raccordement
Accessories:
Clamp connection:  Cu 120-240mm² s(r), f+AE; lam. Cu 21x1-14; 6-8Nm torque
single wedge clamp terminal: Cu, Al* 120-240mm² s(r), s(s), f, f+AE; 6-8 Nm torque
double wedge clamp terminal: Cu  2x 70-120mm² s(r), s(s), f+AE;  6-8Nm torque

*Connections are not maintenance-free if aluminium conductors are used.

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Protection contre les contacts directs:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Couvercle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Platine adaptateur:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Vis de raccordement:
	screw M10, galvanized, chromized

Miscellaneous 
Disconnectors are equipped with arc chambers.
The shock protection is split into 2 for safe connection of the conductors.

Brand 
Woehner or equivalent

Référence
33326000