Text for specification

Désignation
QUADRON®Panel Speed
sectionneur avec fusibles à 3 pôles
borne à cage
taille 00

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	125 A
Tension assignée (IEC) CA:	690 V

AC-23B (690V/125A)
AC-23A (500V/125A)
AC-22A (690V/125A)

2 current paths (L1,L3) in series
DC-22B (220V/125A)

3 current paths in series
DC-22B (440V/63A)

power dissipation at full load of the item:	25,4 W

rated isolation voltage Ui AC:	800 V
Tension assignée de tenue aux chocs Uimp:	8 kV

Fuses gL/gG, size 00, 690V/125A for fuse links IEC 60269-2 / DIN VDE 0636-2 size 00 up to 10W power dissipation

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, dependent upon installation in the connection area; shock protection to DIN EN 50274

Points de raccordement
Box terminal:
1.5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable 
1.5 - 10mm² solid round
16 - 70mm² stranded round 
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x10 - 2x35mm² flexible, identical cables placed side by side square

lam. Cu. 9-13 mm wide 
Terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Charactéristiques des matériaux
Embase:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Couvercle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category &quot;A&quot;
Can be locked in neutral position with up to 3 padlocks
FLAG indicator shows the switch setting
Fuses can be changed safely and without tools thanks to double-breaking main contacts
Additional visible separating section by removing the cover incl. fuses
Can be used as mains disconnector as per IEC / EN 60204-1 (main switch)
Mains switch only in combination with AC-23A/B
Compact dimensions (106mm wide)

Brand 
Woehner or equivalent

Référence
33502000