Text for specification

Désignation
AMBUS^®Panel
support pour fusibles cylindriques, pour fusibles semi-conducteurs
14 x 51 / 1P
50 A / 690 V

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB), CSA, UL, CCC

Charactéristiques électriques
Courant assigné (IEC):	50 A
Tension assignée (IEC) CA:	690 V

rated current (UL):	50 A
rated voltage (UL) AC:	600 V
rated voltage (UL) DC:	600 V

power dissipation at full load of the item:	0,9 W

rated isolation voltage U_i AC:	800 V
Tension assignée de tenue aux chocs Uimp:	6 kV

Icc:	100 kA

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 5W for gG/gL
up to max. 3W for aM
for fuse links aR / gR / gRL under operating conditions up to max. 6.5W, for which at least 25mm² leads must be connected

Points de raccordement
bornes à cage :
1,5 - 35 mm² / AWG 14 - AWG 2 
câble souple, direct ou avec embout
Md 2,5 - 3,0 Nm / 22 - 26 lb.in.

(câble souple de section maxi ne convient pas si équipé d'embout)

Miscellaneous 
large clamping range
 holder for label

Brand 
Woehner or equivalent

Référence
31278000