Text for specification

Désignation
SECUR®Panel
sectionneur à fusibles D0 jusqu'à 63 A
3P

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	63 A
Tension assignée (IEC) CA:	400 V
Tension assignée (IEC) CC:	130 V

AC-22B

power dissipation at full load of the item:	7,8 W

rated isolation voltage Ui AC:	500 V
Tension assignée de tenue aux chocs Uimp:	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638 : AC-22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Points de raccordement
box terminal :
1,5 - 35 mm²    flexible cables, directly or with wire-end ferrule
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
1,5 - 10 mm²    solid
Md 2,5 - 3 Nm

2 cables can be connected, when both chambers of the terminal are used
the maximum combination is 35mm² + 16mm²

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Référence
31314000A