Text for specification

Désignation
SECUR^®60Classic PowerLiner
interrupteur-sectionneur à fusibles D0 pour jeu de barres
pour fusibles D01 et D02, avec LED
E18 / 63 A / 3P
60Classic

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
VDE, CCC

Charactéristiques électriques
Courant assigné (IEC):	63 A
Tension assignée (IEC) CA:	400 V
Tension assignée (IEC) CC:	110 V

AC-23A (400 V)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

power dissipation at full load of the item:	10,5 W

rated isolation voltage U_i AC:	500 V
Tension assignée de tenue aux chocs Uimp:	6 kV

LED indicates blown fuse, operating range: 110 - 400 V AC / DC

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Brand 
Woehner or equivalent

Référence
31525000