Text for specification

Désignation
CAPUS®Panel
sectionneur avec fusibles à 3 pôles
vis M12, poignée gris graphite
taille 3

Normes
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approbations
IEC (CB)

Charactéristiques électriques
Courant assigné (IEC):	630 A
Tension assignée (IEC) CA:	690 V

AC-23B (690V)
AC-22B (690V)
AC-21B (690V)

power dissipation at full load of the item:	268,0 W

rated isolation voltage Ui AC:	1000 V
Tension assignée de tenue aux chocs Uimp:	12 kV

Mechanical lifespan (switching operations) 4000

conv. therm. current in housing
630 A, horizontal installation (adjacent poles) encapsulated 756 x 378 x 428 mm
470 A, vertical installation (poles beneath each other) encapsulated 600 x 600 x 400mm

Shock protection at front with terminal space cover IP20

for fuse links DIN 43620 size 3 up to 48W power dissipation

Points de raccordement
vis M12 :
Md 36 - 44 Nm

Miscellaneous 
double-breaking main contacts,
visible separation sections,
user-independent switching,
voltage-free exchange of fuses
assembly and connection material contained in scope of delivery.

Brand 
Woehner or equivalent

Référence
33340000