Text for specification

Descrizione
CRITO®30Compact
modulo di connessione
morsetti a molla 1,5 - 16 mm², AWG 14 - 6
3p
30Compact 3P

Norme
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Omologazioni
UL

Valori elettrici
corrente nominale (IEC):	63 A
tensione nominale (IEC) AC:	690 V

corrente nominale (UL):	48 A
tensione nominale (UL) AC:	600 V
corrente d'impiego max. (IEC):	80 A

tensione nominale di isolamento Ui AC:	800 V
tensione max. ammissibile (IEC) AC:	800 V
tensione max. ammissibile (IEC) DC:	800 V

resistenza nom. alla corrente di picco Ipk max.:	10 kA

SCCR: 50 kA with JDDZ fuse Class J 60 A / 600 V AC, 35 kA with any DIVQ/7 circuit breaker 60 A / 480 V AC  

Connessioni
for leads as per IEC :
Cu 1.5 - 16mm²
round conductor solid or stranded, flexible, direct or with wire-end ferrule

for leads as per UL :
Cu AWG 16 - 6
Class B (UL486E)

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Coperchio:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Brand 
Woehner or equivalent

Cod. art.
01562000A