Text for specification

Descrizione
CRITO^®60Classic
Piastra con morsetti di connessione, 3 poli
lam. Cu. 20 - 32 x 3 - 15
60Classic

Norme
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Valori elettrici
corrente nominale (IEC):	550 A
tensione nominale (IEC) AC:	690 V
corrente d'impiego max. (IEC):	800 A
tensione max. ammissibile (IEC) AC:	1000 V
tensione max. ammissibile (IEC) DC:	1500 V

resistenza nom. alla corrente di picco I_pk max.:	63.1 kA

Connessioni
bandelle flessibili da 3 x 20 x 1 a 10 x 32 x 1

Proprietà materiali
Corpo base:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Copertura:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free

Terminals: 	galvanised steel, chromited screw: 	hexagon socket screw, galvanised, chromited, thrust piece 	brass, nickel-plated

Miscellaneous 
also rigid copper busbars can be connected if they are installed without mechnical tension 

Brand 
Woehner or equivalent

Cod. art.
01753000